## HARA
Hazard analysis and risk assessment — pressure transmitter
ID | Malfunction | Operational Situation | Hazardous Event | Severity | Exposure | Controllability | ASIL | Safety Goal ID | Safety Goal | Safe State | FTTI
HE-001 | Pressure reading too low | Pump running at full load | Overpressure not detected, vessel bursts | S3 | E4 | C3 | ASIL D | SG-01 | Prevent undetected overpressure | Alarm current < 3.6 mA | 100 ms
HE-002 | Pressure reading frozen | Batch filling | Overfill not detected | S2 | E3 | C3 | ASIL B | SG-01 | Prevent undetected overpressure | Alarm current < 3.6 mA | 100 ms
HE-003 | Spurious alarm | Normal operation | Unplanned shutdown | S1 | E4 | C2 | QM